## Slide 1: NFPA 70E
Standard for Electrical Safety in the Workplace.

## Slide 2: Types of Electrical Hazards
Two Primary Electrical Hazards
  Shock – Injury by contact with energized electrical conductors and circuit parts
  “Electrocution” means death by electricity
  Arc Flash – the passage of substantial electrical current through the air
    Flash
    Blast

## Slide 3: Shock Hazard Thresholds
AC
  >50V and > 5mA
DC
  >100V and >40mA
Capacitors (Reminder, ELC125 to become qualified worker to work on capacitors exceeding threshold below hazardous energy)
  ≤100V and >100J (joules)
  >100V to 400V and > 1J
  >400V and > .25J

## Slide 4: Effects of Shock
Short term effects
  Confusion
  Muscular Pain
  Vision abnormalities
  Swelling
  Headache
  Cardiac irregularities/heart stoppage
  Burns/heating of the body
Long term effects
  Paralysis
  Speech or writing impairment
  Damage to nervous system

## Slide 5: Shock injures the body in two ways
Surface Burns
  Caused by entrance & exit of electrical currents though the body
  Can be caused by a very small amount of current
  1st degree to 3rd degree

## Slide 6: Shock injures the body in two ways
Internal Tissue Damage
  Caused by current flowing through organs of the body
  Results in internal heating which can result in significant burns
  Can continue for minutes/hours/days after contact

## Slide 7: Shock Severity Factors
Shock severity factors depend on:
  Duration of the shock – longer is worse
  Magnitude of the shock – higher current is worse
  Path of current flow – through the heart is worse
  Note: AC and DC are both considered hazardous, however AC disrupts the rhythm of the heart and is considered significantly more dangerous

## Slide 8: Charles Dalziel
Invented the Ground Fault Circuit Interrupter (GFCI)
Professor of Electrical Engineering & Computer Sciences at UC Berkeley
Studied effects of electricity on animals & humans
1904 – 1986

## Slide 9: Charles Dalziel’s Method
Used healthy human subjects
Held copper wire with one hand and placed other hand on grounded brass plate
Current sent through the body, in increased doses, until the subject could no longer hold the plate
Assistants then held subject’s hands on brass plates until they could no longer drop the wire = no let go threshold
Experiment was repeated on dogs, pigs, calves and sheep

## Slide 10: Dalziel on DC
“Tests using gradually increasing direct current produces sensations of internal heating rather than severe muscle contractions…The muscular reactions when the test electrode was released at the higher values were objectionable and sooner or later all subjects declined to attempt higher currents…Tests were conducted on 28 men, and in each case little difficulty was experienced in releasing the electrode. The maximum a subject could tolerate and release was termed his “release current” since this represents a psychological limit rather than the physiological limit of the let-go tests.”

## Slide 11: Levels of Concern AC
(normal adult resistance level)

## Slide 12: AC Shock Approach Boundary Table

## Slide 13: DC Shock Approach Boundary Table

## Slide 14: Where does Energized Work Start?
NFPA 70E (2021) Article 110 (Work involving Electrical Hazards) states that
110.3 Electrically Safe Working Conditions. Energized electrical conductors and circuit parts operating at voltages equal to or greater than 50 volts shall be put into an electrically safe work condition before an employee performs work if any of the following exist:
  (1)The employee is within the Limited Approach Boundary (LAB).

## Slide 15: Boundary's
Limited approach boundary
Restricted approach boundary

## Slide 16: Arc Flash Risk
An undesired electric discharge that travels through the air between conductors, or from a conductor to a ground. The resulting explosion can cause fires and serious harm to equipment and people. The temperature of an arc flash may exceed 35,000 degrees Fahrenheit, which is capable of vaporizing metal and sending a blast of plasma and molten metal in all directions with extreme force.
NFPA70E says that…
“an arc flash hazard may exist when energized electrical conductors or circuit parts are exposed or when they are within equipment in a guarded or enclosed condition, provided a person is interacting with the equipment in such a manner that could cause an electric arc. Under normal operating conditions, enclosed energized equipment that has been properly installed and maintained is not likely to pose an arc flash hazard.”

## Slide 17: Arc-Flash
The dangerous condition associated with the possible release of energy caused by an electric arc and resulting in the following:

## Slide 18: Arc Flash…slow mo

## Slide 19: Arc Flash While Racking Breaker

## Slide 20: Three Factors Affecting Arc Energy
Available Short Circuit Current
  High is typically worse – large amounts of energy is released
Duration
  Long time for protective equipment to operate
  (fuse blow or breaker trip) is worse
Distance
  Closer to the arc is worse

## Slide 21: Burns from the Arc
First Degree – surface only
  skin is red & tender
Second Degree – blistering of the skin
  “Curable burn”
  most painful because nerves are still intact
Third Degree – complete destruction of skin
  charring of tissue
  most dangerous – susceptible to infection
  skin cannot heal itself; complete destruction; nerves severed
Fourth Degree - Extends through entire skin, and into underlying fat, muscle and bone
  Often results in amputation, functional impairment, or death

## Slide 22: Warning
Warning: the next few pictures are extremely graphic. If you are easily disturbed by pictures of injuries, please look away.

## Slide 23: First and second degree burn.

## Slide 24: 3rd and 4th degree burns.

## Slide 25: Injury that happened to a friend of mine.

## Slide 26: New breaker

## Slide 27: Circuit breaker that had an arc flash

## Slide 28: Left hand

## Slide 29: Right hand

## Slide 30: Right hand cleaned up.

## Slide 31: Following the hierarchy of Control

## Slide 32
Example of Elimination:
  Never work with equipment energized
  Non-contact Rotation meter
Example of Substitution:
  Using hazardous voltage for control power?
  Substitute the 120V AC control voltage with 24V DC lowers the voltage exposure to below what is considered hazardous
  Replace electrically powered control with pneumatic

## Slide 33
Physical barrier or other control designed into the system or process to protect the worker. There are two types of Engineering Controls:
  Passive control always present example are barriers, insulation
  Active control require some sort of initiation. One example is a safety interlock (not engaged until a door is opened)

## Slide 34: Finger Safe Terminals

## Slide 35: Lock Out Tag Out = Establishing an Electrically Safe Work Condition
Electrically Safe Work Condition (de-energized):
  Electrical conductors or circuit part have been disconnected from energized parts.
  Locked and tagged
  Tested to ensure the absence of voltage
  Grounded if necessary.
Per NFPA 70E (2021)

## Slide 36: The last line of defense!

## Slide 37: Rubber Insulating Gloves (shock)

## Slide 38: What class is it?
Class of glove defines maximum use voltage

## Slide 39: PPE for Shock
Ensure date has not expired. Once in service, they must be tested every 6 months or annually if not used.

## Slide 40: Zero Energy Verification- Meters
Zero-Energy Verification
  Meter must be a contact-type meter (not induced/proximity) to verify zero energy
  Proximity testers confirm the presence of voltage, not the absence
  Limited conditions of use for proximity testers

## Slide 41: What Safe Work Practices Protect You from Arc-Flash Injuries?
Eliminating the hazard
Increase the working distance between you and the equipment by remote operation of the breaker/disconnect (outside the arc-flash boundary)
Placing circuits in electrically safe working conditions by locking out and tagging out all sources
The use of arc-rated PPE

## Slide 42: What Safe Work Practices Protect You from Shock Injuries?
Use rated barriers to shield worker from exposure
Placing circuits in electrically safe working conditions by locking out and tagging
out all sources
Electrically Insulating gloves
Substituting voltage level to a lower less hazardous voltage

## Slide 43: LOCK OUT TAG OUT
Chose the proper equipment for your task.

## Slide 44: LockOut TagOut
Why LOTO?
NFPA70E (2021)Article 110.3 Establishing an Electrically Safe Working Condition: Energized electrical conductors and circuits parts operating at voltages equal to or greater than 50 volts shall be put into an electrically safe work condition before an employee performs work if any of the following conditions exist:
The employee is within the limited approach boundary.
The employee interacts with conductors or circuit parts that are not exposed but an increased likelihood of injury from an exposure to an an arc flash hazard exists.

## Slide 45
LockOut TagOut
NFAP70E (2021) Article 120.5 Verification an Electrically Safe Work Condition shall be achieved when performed and verified by the following steps:
  Determine all possible sources of electrical supply to the equipment.
    Check applicable drawings, manuals, and diagrams
    Back up systems or generators?
  Properly shutting down the equipment
  Open the disconnecting device (s) for each source with appropriate PPE
    OSHA 1910.147 does not allow you to take credit for
      Interlocks
      Control power fuses
      Control Circuity

## Slide 46
LockOut TagOut
  Apply lockout/tagout devices
    Attach your lock, lock identifying label and “Danger do not Operate” tag.
    Release any stored electrical energy or where the possibility of induced voltage apply ground connecting devices.
  Verify zero-energy
    Use adequately rated contact meter test phase to phase and phase to ground
    Before and after determine that the meter is operating correctly through verification on a known voltage source

## Slide 47
LockOut TagOut
Perform your service, adjustment or maintenance activity
  When finished with task:
    Inspect the work area to ensure that nonessential items have been removed
      grounds
      tools
    Check the work area to ensure that all individuals are clear of the area
    Remove your lock and tags
    Notify affected workers that LOTO has been removed
    Re-Energize